Integrated Gasification Combined Cycle (IGCC) Process Simulation and Optimization

F. Emun, M. Gadalla, L. Jiménez

Department of Chemical engineering, School of Engineering, University Rovira i Virgili, Av. Països Catalans 26, 43007 Tarragona, Spain

Abstract

Integrated Gasification Combined Cycle (IGCC) technology is increasingly important in the world energy market, where low-cost opportunity feedstocks such as coal, heavy oils and pet coke are among the best alternatives. IGCC technology produces low-cost electricity while meeting strict environmental regulations. To further improve IGCC’s efficiency, operating the process at the optimum values, process integration and modifications of the process flow diagrams are typical approaches, where process simulation is used as a tool for implementation. A process simulation model is developed with Aspen Plus( for IGCC system employing Texaco gasifier. The model is applied to conduct sensitivity analyses for key performance parameters and integration options to improve system efficiency and environmental performance. As a result, a significant improvements in process efficiency and environmental performance is attained. Thermal efficiency as high as 45% can be reached and a significant decrease in CO2 and SOx emissions is observed. The CO2 and SOx emission levels reached are 698 kg/MWh and 0.15 kg/MWh,  respectively.

Keywords: IGCC, Process simulation, Process Optimization, Process Integration

Introduction

Increasingly expensive oil and global warming are causing an energy revolution by requiring oil to be supplemented by alternative energy sources and efficient utilization of existing energy sources (e.g. coal, natural gas, nuclear power). Due to the availability and relatively wide geographic distribution, coal is a representative energy source for power generation. The emission of different pollutants, specially green house gases, urged the environmental regulations to be a strong driver for new developments. These developments aim principally at coal based electric power technologies, where IGCC is an alternative technology to pulverized coal (PC) combustion systems [1]. The reason is that IGCC have the potential to obtain higher efficiency and better environmental performance for power generation. They also offer greater fuel flexibility (biomass, refinery residues…) and can offer multiple products (electricity, hydrogen and other chemicals like methanol and higher alcohols) and byproducts (sulfur, sulfuric acid, slag…). In addition, IGCC technology has the potential for CO2 sequestration [1, 2] .

This paper presents an optimization scheme for IGCC through process simulation and sensitivity analysis of the key operating parameters. Then a heat integration scheme is presented for the different sections of the process.

IGCC Process Description and Modeling

IGCC is developed for a Texaco gasifier with radiant/convective cooling system. The process flow diagram is shown in Figure 1. The coal, (Illinois #6), is crushed and mixed with water to produce a slurry (35.5 % w/w water) and pumped into the gasifier with oxygen. The gasifier operates in a pressurized, down flow, entrained design and gasification takes place rapidly at temperatures higher than 1200 ºC. The raw fuel gas produced is mainly composed of H2, CO, CO2, and H2O. The coal's sulfur is primarily converted to H2S and smaller quantity of COS. This raw fuel gas leaves the gasifier at 1370 ºC along with molten ash and a small quantity of unburned carbon. No liquid hydrocarbons are generated.

This gas/molten solids stream enters to a radiant syngas cooler (RSC) and convective syngas cooler (CSC) sections. In this design, the mix of gas/solids from the gasifier enters a radiant syngas cooling (RSC) system where cooling ((815 ºC) is accomplished by generating a high-pressure steam. A convective syngas cooling (CSC)/gas scrubbing system cools the raw fuel stream to about 150 ºC (27.5 bars) by generating additional steam. It uses a gas scrubber and a low temperature gas cooling/heat recovery section to reduce the raw fuel gas stream to 40 oC, prior to entering a cold gas cleaning unit (CGCU) for sulfur removal.

The properties of Illinois #6 coal and the data are reported by the Process Engineering Division of the American Energy Institute (2000) [3]. Some data (operating conditions, range of variables) are retrieved from the literature [4-6].

Figure 1. Simplified diagram for IGCC [7].

Methodology

The flowsheet has several naturally grouped sections: coal preparation, gasification, gas cooling and cleaning, acid gas removal, gas turbine, HRSG, steam cycle, etc... All sections were rigorously modeled using Aspen Plus(.

Simulation was controlled using FORTRAN routines and design specifications to reduce the number of initial conditions and to adjust automatically those associated variables. The main functional relationships (i. e. control structures) are: the amount of coal input is a function of the gas turbine net power (272 MW), the amount of slurry water depends of the coal input (35.5 %), the make-up water for the steam cycle depends on the temperature of the stack gas (125oC), the air input to the ASU is determined by the gasifier net duty and the air to the gas turbine (GT) combustor is fixed by the combustor net heat duty or the stoichiometric amount of air required.

Since this is a large and complex model (seven nested loops, five control blocks and many design specifications) it is very sensitive towards the loop’s break points (i. e. tear streams) and their initial conditions. After detailed analysis, a specific computational sequence was set up for the model, and the ranges of initial conditions were established to improve the convergence. Sensitivity analysis and process integration are applied to improve the efficiency and environmental performance of the process.

Process Optimization

The sensitivity of the process for different variables is analyzed. The variables studied are: gasification temperature, combustion temperature, level of N2 injection and solid concentration of the coal slurry. The main parameters analyzed within each analysis are thermal efficiency (LHV) ((LHV), cold gas efficiency ((CG), net power output per ton of coal, O2:carbon ratio (O2:C) and air:clean syngas ratio (air:syn).

Effects of Gasification Temperature

The sensitivity of the process for the gasification temperature is done under the operational range of temperatures where gasification can take place with slagging of the ash (1250 ºC and 1550 ºC) [1]. As the gasification temperature increases, the thermal efficiency decreases due to a decrease in the cold gas efficiency. This decline in cold gas efficiency is due to a rise in the O2:C ratio in order to combust more carbon to reach high temperature. On the contrary, the total net power increases because the steam turbine power output rises due to a higher amount of the slurry used for the same quantity of gas turbine output; however, the net power output per ton of coal consumed has  a decreasing trend as the thermal efficiency.

The CO2 and SOx emissions per unit of power output increases due to the rise in the coal consumption for the same level of GT power output. But the NOx emission per unit of power output decreases very slightly due to a decline in the air:clean syngas ratio, thereby lessening the thermal NOx formation.

Effects of Gas Turbine Inlet Temperature (Syngas Combustion Temperature)

The analysis is performed for a range of temperatures (Tcomb) around the base case (1250-1550 oC). For an increase in Tcomb by 300 oC, thermal efficiency ((LHV) increases by 5%. Along with an increase in (LHV, the CO2 and SOx emissions per unit power output also decrease. This is due to the decrease in the level of coal consumption for the same GT power output. But, the NOx emission increases because of an increase in thermal NOx formation at higher temperatures. The carbon conversion efficiency, the cold gas efficiency and the O2:C ratio remain almost constant because they are independent of the combustor operating temperature.

Effects of Level of N2 injection

As the fraction of N2 injection to the GT combustor increases:

The thermal efficiency increases, due to a decrease in the slurry (coal) requirement as more N2 is used to drive the turbine.

The net power output decreases due to a decrease in the steam turbine power output as a result of the reduction in the coal flow.

The net power output per ton of coal input increases because of the decrease in coal requirement for the same level of GT output.

The CO2, SOx and NOx emissions decrease due to the decrease in the coal consumption and the diluting effect of the N2, thus inhibiting thermal NOx formation.

The carbon conversion efficiency, the cold gas efficiency and the O2:C ratio remain constant because they are independent of the varying parameter.

Effects of Solid Concentration in Coal Slurry

With the rise in solids concentration, the O2:carbon ratio decreases because the required energy to vaporize and superheat the water decreases. Therefore the syngas heating value increases because less coal is being used to supply energy for the gasification.

Due to this, the thermal efficiency and the net power output per ton of coal input increase. The emissions per unit power of CO2, SOx and NOx slightly increase because of the slight decrease in the total net power. The net power gets minimized with the rise in solids concentration because the amount of steam produced in the HRSG gets down as the coal consumption decreases.

Simultaneous analysis of the effects of Level of N2 injection and Syngas Combustion Temperature

The thermal efficiency increases almost linearly with the increase in the combustor temperature for all levels of N2 injection to the combustor (Figure 2). Therefore, the power augmenting effect of the N2 flow is greater than its diluting effect in the combustor.

Figure 2. Effects of simultaneous variations of the level of N2 injection and combustion temperature on the thermal efficiency.

N2 injection level of 98% represents the practical upper bound on the total amount of N2 available for injection, as venting is inevitable and N2 can be used as a coolant in the gas turbine [4]. This value supposes that the combustor operates at the highest possible temperature (depending on the turbine inlet temperature specification), thus producing power with relatively high thermal efficiency.

Heat Integration

With the aim to improve thermal efficiency and environmental performance, the effects of heat integration of the gasifier and GT combustor is analyzed. This study is complemented by the integration of the air separation unit (ASU) and the gas cleaning unit.

Heat integration of the Gasifier and the GT-Combustor

In this analysis, the gasifier is heat integrated with the GT-combustor and the level of integration is optimized by varying the oxygen and air requirements of the gasifier and combustor, respectively. As the gasification reaction is endothermic, its net heat duty is kept zero so that no external heat is added to the system (except from the combustor).

Figure 3. Dependence of  a) Thermal efficiency; b) Cold gas efficiency and carbon conversion efficiency; on heat integration of GT-combustor and gasifier.

Table 1. Stream data for the heat integration

|  | Optimized Texaco gasifier | Heat integrated case |
| --- | --- | --- |
|  | Tin(oC) | Tout(oC) | Duty(MW) | Tin(oC) | Tout(oC) | Duty(MW) |
| Cond. regen. | 347 | 332 | -12 | 347 | 332 | -12 |
| Oxygen | 150 | 150 | 0 | 150 | 340 | 5.8 |

Figure 4. The sensitivity of the combustor and gasifier level of integration for the case of ASU and gas cleaning units heat integration.

With the increase in the level of heat integration, the net power output increases, but the net power per ton of coal consumed increases until it reaches a flat maximum (Figure 3a). The decrease in the O2:C ratio with the increase in the level of integration has a positive effect on the thermal efficiency at first, because it favors the gasification reaction (compared with the combustion reaction) and increases the cold gas efficiency. Then, with further decrease in the O2:C ratio, the carbon conversion efficiency and, in turn the cold gas efficiency, start to decrease (Figure 3b), thereby decreasing the thermal efficiency. The air requirement in the combustor also decreases as the net heat duty of the combustor increases. The last effect is to minimize the heat absorbed by the excess air, to maintain the operating temperature.

Heat integration of the air separation unit (ASU) and the gas cleaning unit

The oxygen from the ASU to the gasifier is heat integrated with the condenser of the amine regenerator (condenser regenerator)  in the gas cleaning unit. This is proposed due to the availability of high quality heat from the amine regenerator unit (Table 1).

The integration is done together with the analysis of the sensitivity of the process for the level of combustor and gasifier integration which is already done in section 5.1.

As shown by Figure 4, the trend is similar with the previous analysis, and the maximum is shifted to the left and the efficiency improved. The maximum efficiency is reached at a combustor duty of 150MW (unlike 200MW in the previous case) due to the further decrease in the O2:C ratio as the O2 inlet temperature to the gasifier increases.

Conclusions

Sensitivity of the process for different operating variables has been studied by taking the best case (i. e. with high efficiency) as a base for the next analyses. At the end of these analyses, the maximum thermal efficiency (LHV) attained is 45% with CO2 and SOx emissions of 698 kg/MWh and 0.15 kg/MWh, respectively. This result corresponds to a gasification temperature of 1250 ºC, a combustion temperature of 1550 ºC, 98% of N2 injection to the GT combustor, and a slurry solid concentration of 80%. For a practical application of this improvement, among other considerations like the capacity of the equipments and their cost, the flowability of the slurry at the high level of solids has to be considered.

Heat integration of the gasifier and the combustor has revealed that the best value of net heat duty for the integration is around 200 MW; but, the analysis for the heat integrated case of the ASU and the gas cleaning units reveals that the best value of net combustor duty for the integration is 150 MW. Figure 3 shows that the slope of variation in thermal efficiency is very high in the  right side of the maximum and therefore a slight variation in operating conditions could lead to a significant loss of efficiency. Therefore, it is advisable to operate at a slightly lower value of the net duty those problems during operation.

Acknowledgement

F. Emun wishes to express his gratitude for the financial support received from the Agencia de Gestió d’Ajuts Universitaris i de Recerca (AGAUR) from Generalitat de Catalunya.

References

L. Zheng, E. Furinsky, 2005, Comparison of Shell, Texaco, BGL and KRW gasifiers as part of IGCC plant computer simulations, Energy conversion and management, 46, 2005, 1767-1779.

G. Ordorica-Garcia, P. Douglas, E. Croiset, L. Zheng, 2005, Technoeconomic evaluation of IGCC power plants for CO2 avoidance, Energy conversion and management, 47, 2006, 2250-2259.

W. Shelton , J. Lyons, 1998, Texaco gasifier base cases PED-IGCC-98-001, US Department of Energy, Process Engineering Division, 2000, 1-52.

H. Christopher, Y. Zhu, 2006, Improved system integration for integrated gasification combined cycle (IGCC) systems, Environ. Sci. Technol., 40, 2006, 1693-1699.

S. Sugiyama, N. Suzuki, Y. Kato, K. Yoshikawa, A. Omina, T. Ishii, K. Yoshikawa, T. Kiga, 2005, Gasification performance of coals using high temperature air, Energy, 30, 2005, 399-413.

J. Minchener, 2004, Coal gasification for advanced power generation, Fuel, 84, 2005, 2222-2235.

G. Booras, N. Holt, 2004, Pulverised coal and IGCC plant cost and performance estimates, Gasification technologies conference, Washington DC, October 2004.